## Instructions
Fault Locator | Disclaimer: This program is provided as is, without warranty, either expressed or implied. It does not purport to be free of bugs. Therefore, its use is the sole responsibility of the user.
By: Alex Rangel
Schweitzer Engineering Laboratories, Inc.
Fault Locator
This program calculates the fault location using V2 and I2 from each end of the line.
Instructions:
1. Insert I2 and V2 from the left relay at I2S and V2S, respectively.
2. Insert I2 and V2 from the right relay at I2R and V2R, respectively.
3. Insert the total line length in miles, CTR, and PTR.
4. Specify the line impedance format.
5. Insert the line impedance settings in polar or rectangular form.
6. The answer is expressed in per unit (m) and in miles.

## Calculator
Fault Locator
|  | Magnitude | Angle |  | Real | Imaginary
| I2S | 400 | 284.7 |  | 101.5032 | -386.9071
| V2S | 12000 | 184 |  | -11970.7686 | -837.0777
| I2R | 800 | 280.1 |  | 140.2934 | -787.6025
| V2R | 15800 | 183.5 |  | -15770.5298 | -964.5669
| Z2L | 10.575 | 83.5 |  | 1.1971 | 10.507
| Line Length | 17.6 | miles
| CTR | 400
| PTR | 3000
LINE IMPEDANCE SETTINGS
|  | Polar Coordinates |  | OR | Rectangular Coordinates
|  | Z1MAG | 1.41 |  | R1 | 0
|  | Z1ANG | 83.5 |  | X1 | 0
| Main Method |  |  |  | Alternate Method
| Fault | 17.015 | miles from left |  | Fault | 17.0169 | miles from left
| Location | 0.58501 | miles from right |  | Location | 0.58312 | miles from right
| m (distance in pu) | 0.96676 | per unit from left |  | m | 0.96687 | per unit from left
| 1-m | 0.033239 | per unit from right |  | 1-m | 0.033132 | per unit from right
**
| Calculations for Main |  |  | Calculations for Alternate |  |  |  | For hiding blocks
| A | 53678700 |  | 0.96687 |  |  |  | 1
| B | -511726158.5519 | [5 empty] | 2
| C | 444547192.8241 |  | Rectangular calculations for V and I
| m1 | 8.5664 |  |  |  | Rectangular
| m2 | 0.96676 |  |  |  | 101.503177833922-386.907101110351i
-11970.7686031179-837.077684929503i
140.29338087359-787.602543979549i
-15770.5298150655-964.56692465074i
1.19712398559561+10.5070223737799i
[5 empty] | Z2S_S | 5.5699984615673+29.4783838963085i
[5 empty] | Z2S_R | 2.27000872223412+19.6191121206078i
**

## Revisions
Revision History
Date | Changes
2012-12-05 | Initial Version

## Sheet3
box 1 | 1
Box 2 | 2