## Z2 calcs
Enter SEL-321 Relay Settings |  |  | Intermediate Calculations
Z1ANG = | 85 | ° | deg = | π/180 = | 0.017453
CTR = | 400 | 1
PTR = | 2000 | 1 | V2 = | -2.76552735366639+0.438016502112647i
Z2F = | 3 | Ω (secondary) | I2 = | -0.00966888285225795+0.0919932753215653i
50QF = | 0.5 | amps (secondary)
Z2R = | 6 | Ω (secondary) | 1<Z1ANG = | 0.0871557427476581+0.996194698091746i
50QR = | 0.25 | amps (secondary) | 1<Z1ANG * I2 = | -0.0924859118019663-0.00161434759544873i
a2 = | 0.1 |  | (1<Z1ANG * I2)* = | -0.0924859118019663+0.00161434759544873i
Enter Negative-Sequence Voltage & Current2 |  |  | Z2m = | 30.2703 | 4.4538
¦V2¦ = | 5.6 | kV (primary)1
ang V2 = | 171 | ° | Calculate secondary V2 & I2
¦I2¦ = | 37 | amps (primary)1 | ¦I2sec¦ = | 0.0925 | amps (secondary)
ang I2 = | 96 | ° | ang I2sec = | 96 | °
Dynamic Directional Thresholds |  |  | ¦V2sec¦ = | 2.8 | volts (secondary)
Z2FT = | -3.8176 | Ω (secondary) | ang V2sec = | 171 | °
Z2RT = | 12.0676 | Ω (secondary)
Calculate Graph Data
Calculated Z2 |  |  |  | Y
Z2c = | 29.8104 | Ω (secondary) | X | Z2F | Z2R | Z2FT | Z2RT | Z2c
|  |  | -18 | 3 | 6 | -3.8176 | 12.0676
Directional Declaration |  |  | 0 | 3 | 6 | -3.8176 | 12.0676 | 29.8104
Direction = | REVERSE |  | 18 | 3 | 6 | -3.8176 | 12.0676
1 To enter negative-sequence quantities in secondary volts and amps, set CTR = 1 and PTR = 1000.
2 Typically from SEL-5601 Analytic Assistant software phasor screen.

## Z0 calcs
Enter SEL-321 Relay Settings |  |  | Intermediate Calculations
Z0ANG = | 75 | ° | deg = | π/180 = | 0.017453
CTR = | 400 | 1
PTR = | 2000 | 1 | V0 = | -2.6302473018495+0.322953760023641i
Z0F = | 9 | Ω (secondary) | I0 = | 0.143943527881802+0.577325957134218i
50GF | 0.5 | amps (secondary)
Z0R = | 18 | Ω (secondary) | 1<Z0ANG = | 0.258819045102521+0.965925826289068i
50GR | 0.5 | amps (secondary) | 1<Z0ANG * I0 = | -0.520398725747941+0.28846172404657i
a0 = | 0.1 |  | (1<Z0ANG * I0)* = | -0.520398725747941-0.28846172404657i
Enter Zero-Sequence Voltage & Current2 |  |  | Z0m = | 4.4538 | 4.4538
¦V0¦ = | 5.3 | kV (primary)1
ang V0 = | 173 | ° | Calculate secondary V2 & I2
¦I0¦ = | 238 | amps (primary)1 | ¦I0sec¦ = | 0.595 | amps (secondary)
ang I0 = | 76 | ° | ang I0sec = | 76 | °
Dynamic Directional Thresholds |  |  | ¦V0sec¦ = | 2.65 | volts (secondary)
Z0FT = | 10.1366 | Ω (secondary) | ang V0sec = | 173 | °
Z0RT = | 14.6134 | Ω (secondary)
Calculate Graph Data
Calculated Z0 |  |  |  | Y
Z0c = | 4.1295 | Ω (secondary) | X | Z0F | Z0R | Z0FT | Z0RT | Z0c
|  |  | -18 | 9 | 18 | 10.1366 | 14.6134
Directional Declaration |  |  | 0 | 9 | 18 | 10.1366 | 14.6134 | 4.1295
Direction = | FORWARD |  | 18 | 9 | 18 | 10.1366 | 14.6134
1 To enter negative-sequence quantities in secondary volts and amps, set CTR = 1 and PTR = 1000.
2 Typically from SEL-5601 Analytic Assistant software phasor screen.