## Sheet1
Testing Power Element Spreadsheet
Conversion From Primary Power to Secondary Power
|  |  | Set Point (Primary kVA) |  |  | 250000 |  | PHROT | 1
|  |  | CTR |  |  | 200 |  | Type | 1
|  |  | PTR |  |  | 2000 |  | PF | 2
[8 empty] | Phase | 2
|  |  | Calculated Secondary Value (Secondary VA) |  |  | 625 |  | What Phase | 1
[8 empty] | PTCONN | 1
|  |  | Nominal Voltage, L-N (Secondary V) |  |  | 72
Test Quantities
|  |  |  | VA | VB | VC
|  |  | Mag. | 72 | 72 | 72
|  |  | Angle | 0 | -120 | 120
Value | 3-Phase Power Element Pickup (Secondary VA) | 625 |  | IA | IB | IC | Three-Phase Wye & Delta Connected PT
0.95 |  |  | Mag. | 3.0458 | 3.0458 | 3.0458 |  | IA | IB | IC
|  |  | Angle | -18.1949 | -138.1949 | 101.8051 | Pos. WATTS | 3.0458 | 3.0458 | 3.0458
[8 empty] | -18.1949 | -138.1949 | 101.8051
[7 empty] | Neg. WATTS | 3.0458 | 3.0458 | 3.0458
[8 empty] | 0 | 0 | 0
[7 empty] | Pos. VARS | 9.2667 | 9.2667 | 9.2667
[8 empty] | 0 | 0 | 0
[7 empty] | Neg. VARS | 9.2667 | 9.2667 | 9.2667
[8 empty] | 0 | 0 | 0
Single-Phase Testing
[8 empty] | IA | IB | IC
[7 empty] | Pos. WATTS | 9.1374 | 9.1374 | 9.1374
[8 empty] | -18.1949 | -138.1949 | 101.8051
[7 empty] | Neg. WATTS | 9.1374 | 9.1374 | 9.1374
[8 empty] | 0 | 0 | 0
[7 empty] | Pos. VARS | 27.8 | 27.8 | 27.8
[7 empty] | Neg. VARS | 27.8 | 27.8 | 27.8
[8 empty] | 0 | 0 | 0
Power Element Type
+ WATTS
- WATTS
+ VARS
-VARS
Phase Rotation
ABC
ACB
Single-Phase
Three-Phase
Test Method
Power Factor
A-Phase
B-Phase
Test Phase for Single-Phase Element
C-Phase
WYE
DELTA
PTCONN
Pickup Setting
Lead
Lag
Unity
Note on N8: Enter VA primary
Note on N9: Enter CT ratio
Note on N10: Enter PT ratio
Note on N14: Enter nominal line-to-neutral voltage