{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":40,"n_cols":20,"rows_kept":40,"cut":false,"hidden":false,"merged":[[30,15,30,19],[32,15,33,16],[34,15,35,16],[36,15,37,16],[38,15,39,16],[4,10,5,13],[0,1,1,13],[27,15,28,16],[21,15,22,16],[23,15,24,16],[25,15,26,16],[19,15,19,19],[19,7,20,8],[15,10,15,13],[19,4,20,6],[13,10,13,12],[7,10,7,12],[9,10,9,12],[8,10,8,12],[11,10,11,12]]}
[null,"Testing Power Element Spreadsheet"]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,"Conversion From Primary Power to Secondary Power"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,"Set Point (Primary kVA)",null,null,250000,null,null,null,"PHROT",1]
[null,null,null,null,null,null,null,null,null,null,"CTR",null,null,200,null,null,null,"Type",1]
[null,null,null,null,null,null,null,null,null,null,"PTR",null,null,2000,null,null,null,"PF",2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Phase",2]
[null,null,null,null,null,null,null,null,null,null,"Calculated Secondary Value (Secondary VA)",null,null,{"$f":"N8/(N9*N10)*1000","v":625},null,null,null,"What Phase",1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"PTCONN",1]
[null,null,null,null,null,null,null,null,null,null,"Nominal Voltage, L-N (Secondary V)",null,null,72]
[]
[null,null,null,null,null,null,null,null,null,null,"Test Quantities"]
[null,null,null,null,null,null,null,null,null,null,null,"VA","VB","VC"]
[null,null,null,null,null,null,null,null,null,null,"Mag.",{"$f":"IF(AND($S$13=2,$S$11=2),$N$14*SQRT(3),IF(AND($S$13=1,$S$11=2),$N$14, IF(AND($S$13=1,$S$11=1,$S$12=1),$N$14,0)))","v":72},{"$f":"IF(AND($S$13=2,$S$11=2),0,IF(AND($S$13=1,$S$11=2),$N$14, IF(AND($S$13=1,$S$11=1,$S$12=2),$N$14,0)))","v":72},{"$f":"IF(AND($S$13=2,$S$11=2),$N$14*SQRT(3),IF(AND($S$13=1,$S$11=2),$N$14, IF(AND($S$13=1,$S$11=1,$S$12=3),$N$14,0)))","v":72}]
[null,null,null,null,null,null,null,null,null,null,"Angle",{"$f":"IF(AND($S$8=1,$S$13=1,$S$11=2),0,IF(AND($S$8=2,$S$13=1,$S$11=2),0,IF(AND($S$8=1,$S$13=2,$S$11=2),30,IF(AND($S$8=2,$S$13=2,$S$11=2),-30,IF(AND($S$8=1,$S$13=2,$S$11=1),0,IF(AND($S$8=2,$S$13=2,$S$11=1),0,0))))))","v":0},{"$f":"IF(AND($S$8=1,$S$13=1,$S$11=2),-120,IF(AND($S$8=2,$S$13=1,S11=2),120,IF(AND($S$8=1,$S$13=2,$S$11=2),0,IF(AND($S$8=2,$S$13=2,$S$11=2),0,IF(AND($S$13=1,$S$12=2,$S$11=1,$S$8=1),-120,IF(AND($S$13=1,$S$12=2,$S$11=1,$S$8=2),120,0))))))","v":-120},{"$f":"IF(AND($S$8=1,$S$13=1,$S$11=2),120,IF(AND($S$8=2,$S$13=1,$S$11=2),-120,IF(AND($S$8=1,$S$13=2,$S$11=2),90,IF(AND($S$8=2,$S$13=2,$S$11=2),-90,IF(AND($S$8=1,S13=2,$S$11=1),0,IF(AND($S$8=2,$S$13=2,$S$11=1),0,IF(AND($S$13=1,$S$12=3,$S$11=1,$S$8=1),120,IF(AND($S$13=1,$S$12=3,$S$11=1,$S$8=2),-120,0))))))))","v":120}]
[null,"Value",null,null,{"$f":"IF(S11=1,\"1-phase Power Element Pickup (VA, Secondary)\",\"3-Phase Power Element Pickup (Secondary VA)\")","v":"3-Phase Power Element Pickup (Secondary VA)"},null,null,625,null,null,null,"IA","IB","IC",null,"Three-Phase Wye & Delta Connected PT"]
[null,0.95,null,null,null,null,null,null,null,null,"Mag.",{"$f":"IF(AND($S$9=1,$S$11=2,OR($S$13=1,$S$13=2)),$R$22,IF(AND($S$9=1,$S$11=1,$S$12=1,$S$13=1),$R$33,IF(AND($S$9=2,$S$11=2,OR($S$13=1,$S$13=2)),$R$24,IF(AND($S$9=2,$S$11=1,$S$12=1,$S$13=1),$R$35,IF(AND($S$9=3,$S$11=2,OR($S$13=1,$S$13=2)),$R$26,IF(AND($S$9=3,$S$11=1,$S$12=1,$S$13=1),$R$37,IF(AND($S$9=4,$S$11=2,OR($S$13=1,$S$13=2)),$R$28,IF(AND($S$9=4,$S$11=1,$S$12=1,$S$13=1),$R$39,0))))))))","v":3.0458089668615989},{"$f":"IF(AND($S$9=1,$S$11=2,OR($S$13=1,$S$13=2)),$S$22,IF(AND($S$9=1,$S$11=1,$S$12=2,$S$13=1),$S$33,IF(AND($S$9=2,$S$11=2,OR($S$13=1,$S$13=2)),$S$24,IF(AND($S$9=2,$S$11=1,$S$12=2,$S$13=1),$S$35,IF(AND($S$9=3,$S$11=2,OR($S$13=1,$S$13=2)),$S$26,IF(AND($S$9=3,$S$11=1,$S$12=2,$S$13=1),$S$37,IF(AND($S$9=4,$S$11=2,OR($S$13=1,$S$13=2)),$S$28,IF(AND($S$9=4,$S$11=1,$S$12=2,$S$13=1),$S$39,0))))))))","v":3.0458089668615989},{"$f":"IF(AND($S$9=1,$S$11=2,OR($S$13=1,$S$13=2)),$T$22,IF(AND($S$9=1,$S$11=1,$S$12=3,$S$13=1),$T$33,IF(AND($S$9=2,$S$11=2,OR($S$13=1,$S$13=2)),$T$24,IF(AND($S$9=2,$S$11=1,$S$12=3,$S$13=1),$T$35,IF(AND($S$9=3,$S$11=2,OR($S$13=1,$S$13=2)),$T$26,IF(AND($S$9=3,$S$11=1,$S$12=3,$S$13=1),$T$37,IF(AND($S$9=4,$S$11=2,OR($S$13=1,$S$13=2)),$T$28,IF(AND($S$9=4,$S$11=1,$S$12=3,$S$13=1),$T$39,0))))))))","v":3.0458089668615989},null,null,null,"IA","IB","IC"]
[null,null,null,null,null,null,null,null,null,null,"Angle",{"$f":"IF(AND($S$9=1,$S$11=2,OR($S$13=1,$S$13=2)),$R$23,IF(AND($S$9=1,$S$11=1,$S$12=1,$S$13=1),$R$34,IF(AND($S$9=2,$S$11=2,OR($S$13=1,$S$13=2)),$R$25,IF(AND($S$9=2,$S$11=1,$S$12=1,$S$13=1),$R$36,IF(AND($S$9=3,$S$11=2,OR($S$13=1,$S$13=2)),$R$27,IF(AND($S$9=3,$S$11=1,$S$12=1,$S$13=1),$R$38,IF(AND($S$9=4,$S$11=2,OR($S$13=1,$S$13=2)),$R$29,IF(AND($S$9=4,$S$11=1,$S$12=1,$S$13=1),$R$40,0))))))))","v":-18.19488770733096},{"$f":"IF(AND($S$9=1,$S$11=2,OR($S$13=1,$S$13=2)),$S$23,IF(AND($S$9=1,$S$11=1,$S$12=2,$S$13=1),$S$34,IF(AND($S$9=2,$S$11=2,OR($S$13=1,$S$13=2)),$S$25,IF(AND($S$9=2,$S$11=1,$S$12=2,$S$13=1),$S$36,IF(AND($S$9=3,$S$11=2,OR($S$13=1,$S$13=2)),$S$27,IF(AND($S$9=3,$S$11=1,$S$12=2,$S$13=1),$S$38,IF(AND($S$9=4,$S$11=2,OR($S$13=1,$S$13=2)),$S$29,IF(AND($S$9=4,$S$11=1,$S$12=2,$S$13=1),$S$40,0))))))))","v":-138.19488770733096},{"$f":"IF(AND($S$9=1,$S$11=2,OR($S$13=1,$S$13=2)),$T$23,IF(AND($S$9=1,$S$11=1,$S$12=3,$S$13=1),$T$34,IF(AND($S$9=2,$S$11=2,OR($S$13=1,$S$13=2)),$T$25,IF(AND($S$9=2,$S$11=1,$S$12=3,$S$13=1),$T$36,IF(AND($S$9=3,$S$11=2,OR($S$13=1,$S$13=2)),$T$27,IF(AND($S$9=3,$S$11=1,$S$12=3,$S$13=1),$T$38,IF(AND($S$9=4,$S$11=2,OR($S$13=1,$S$13=2)),$T$29,IF(AND($S$9=4,$S$11=1,$S$12=3,$S$13=1),$T$40,0))))))))","v":101.80511229266904},null,"Pos. WATTS",null,{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*$B$21),($H$20/3)/($N$14))","v":3.0458089668615989},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*$B$21),($H$20/3)/($N$14))","v":3.0458089668615989},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*$B$21),($H$20/3)/($N$14))","v":3.0458089668615989}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND($S$10=1,$S$9=1),ACOS($B$21)*180/3.14159,IF(AND($S$10=2,$S$9=1),-ACOS($B$21)*180/3.14159,IF(AND($S$10=3,$S$9=1),ACOS(1)*180/3.14159,0)))","v":-18.19488770733096},{"$f":"IF(AND($S$9=1,$S$10=1,$S$8=1),(ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=1,$S$10=1,$S$8=2),(ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=1,$S$10=2,$S$8=1),(-ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=1,$S$10=2,$S$8=2),(-ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=1,$S$10=3,$S$8=1),(ACOS(1)*180/3.14159)-120,IF(AND($S$9=1,$S$10=3,$S$8=2),(ACOS(1)*180/3.14159)+120,0))))))","v":-138.19488770733096},{"$f":"IF(AND($S$9=1,$S$10=1,$S$8=1),(ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=1,$S$10=1,$S$8=2),(ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=1,$S$10=2,$S$8=1),(-ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=1,$S$10=2,$S$8=2),(-ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=1,$S$10=3,$S$8=1),(ACOS(1)*180/3.14159)+120,IF(AND($S$9=1,$S$10=3,$S$8=2),(ACOS(1)*180/3.14159)-120,0))))))","v":101.80511229266904}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Neg. WATTS",null,{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*$B$21),($H$20/3)/($N$14))","v":3.0458089668615989},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*$B$21),($H$20/3)/($N$14))","v":3.0458089668615989},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*$B$21),($H$20/3)/($N$14))","v":3.0458089668615989}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND($S$10=1,$S$9=2),ACOS($B$21)*180/3.14159+180,IF(AND($S$10=2,$S$9=2),-ACOS($B$21)*180/3.14159+180,IF(AND($S$10=3,$S$9=2),ACOS(1)*180/3.14159+180,0)))","v":0},{"$f":"IF(AND($S$9=2,$S$10=1,$S$8=1),(ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=2,$S$10=1,$S$8=2),(ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=2,$S$10=2,$S$8=1),(-ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=2,$S$10=2,$S$8=2),(-ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=2,$S$10=3,$S$8=1),(ACOS(1)*180/3.14159)-120+180,IF(AND($S$9=2,$S$10=3,$S$8=2),(ACOS(1)*180/3.14159)+120+180,0))))))","v":0},{"$f":"IF(AND($S$9=2,$S$10=1,$S$8=1),(ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=2,$S$10=1,$S$8=2),(ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=2,$S$10=2,$S$8=1),(-ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=2,$S$10=2,$S$8=2),(-ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=2,$S$10=3,$S$8=1),(ACOS(1)*180/3.14159)+120+180,IF(AND($S$9=2,$S$10=3,$S$8=2),(ACOS(1)*180/3.14159)-120+180,0))))))","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Pos. VARS",null,{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*SIN(ACOS($B$21))),($H$20/3)/($N$14*SIN(ACOS(1))))","v":9.2666755674240218},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*SIN(ACOS($B$21))),($H$20/3)/($N$14*SIN(ACOS(1))))","v":9.2666755674240218},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*SIN(ACOS($B$21))),($H$20/3)/($N$14*SIN(ACOS(1))))","v":9.2666755674240218}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND($S$10=2,$S$9=3),-ACOS($B$21)*180/3.14159,IF(AND($S$10=1,$S$9=3),ACOS($B$21)*180/3.14159+180,0))","v":0},{"$f":"IF(AND($S$9=3,$S$10=2, $S$8=1),(-ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=3,$S$10=2, $S$8=2),(-ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=3,$S$10=1, $S$8=1),(ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=3,$S$10=1, $S$8=2),(ACOS($B$21)*180/3.14159)+120+180,0))))","v":0},{"$f":"IF(AND($S$9=3,$S$10=2, $S$8=1),(-ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=3,$S$10=2, $S$8=2),(-ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=3, $S$10=1, $S$8=1),(ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=3,$S$10=1, $S$8=2),(ACOS($B$21)*180/3.14159)-120+180,0))))","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Neg. VARS",null,{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*SIN(ACOS($B$21))),($H$20/3)/($N$14*SIN(ACOS(1))))","v":9.2666755674240218},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*SIN(ACOS($B$21))),($H$20/3)/($N$14*SIN(ACOS(1))))","v":9.2666755674240218},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20/3)/($N$14*SIN(ACOS($B$21))),($H$20/3)/($N$14*SIN(ACOS(1))))","v":9.2666755674240218}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND($S$10=1,$S$9=4),ACOS($B$21)*180/3.14159,IF(AND($S$10=2,$S$9=4),-ACOS($B$21)*180/3.14159+180,0))","v":0},{"$f":"IF(AND($S$9=4,$S$10=1, $S$8=1),(ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=4,$S$10=1, $S$8=2),(ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=4,$S$10=2, $S$8=1),(-ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=4,$S$10=2, $S$8=2),(-ACOS($B$21)*180/3.14159)+120+180,0))))","v":0},{"$f":"IF(AND($S$9=4,$S$10=1,$S$8=1),(ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=4,$S$10=1,$S$8=2),(ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=4,$S$10=2,$S$8=1),(-ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=4,$S$10=2,$S$8=2),(-ACOS($B$21)*180/3.14159)-120+180,0))))","v":0}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Single-Phase Testing"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"IA","IB","IC"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Pos. WATTS",null,{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*$B$21),($H$20)/($N$14))","v":9.1374269005847957},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*$B$21),($H$20)/($N$14))","v":9.1374269005847957},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*$B$21),($H$20)/($N$14))","v":9.1374269005847957}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND($S$10=1,$S$9=1),ACOS($B$21)*180/3.14159,IF(AND($S$10=2,$S$9=1),-ACOS($B$21)*180/3.14159,IF(AND($S$10=3,$S$9=1),ACOS(1)*180/3.14159,0)))","v":-18.19488770733096},{"$f":"IF(AND($S$9=1,$S$10=1,$S$8=1),(ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=1,$S$10=1,$S$8=2),(ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=1,$S$10=2,$S$8=1),(-ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=1,$S$10=2,$S$8=2),(-ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=1,$S$10=3,$S$8=1),(ACOS(1)*180/3.14159)-120,IF(AND($S$9=1,$S$10=3,$S$8=2),(ACOS(1)*180/3.14159)+120,0))))))","v":-138.19488770733096},{"$f":"IF(AND($S$9=1,$S$10=1,$S$8=1),(ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=1,$S$10=1,$S$8=2),(ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=1,$S$10=2,$S$8=1),(-ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=1,$S$10=2,$S$8=2),(-ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=1,$S$10=3,$S$8=1),(ACOS(1)*180/3.14159)+120,IF(AND($S$9=1,$S$10=3,$S$8=2),(ACOS(1)*180/3.14159)-120,0))))))","v":101.80511229266904}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Neg. WATTS",null,{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*$B$21),($H$20)/($N$14))","v":9.1374269005847957},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*$B$21),($H$20)/($N$14))","v":9.1374269005847957},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*$B$21),($H$20)/($N$14))","v":9.1374269005847957}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND($S$10=1,$S$9=2),ACOS($B$21)*180/3.14159+180,IF(AND($S$10=2,$S$9=2),-ACOS($B$21)*180/3.14159+180,IF(AND($S$10=3,$S$9=2),ACOS(1)*180/3.14159+180,0)))","v":0},{"$f":"IF(AND($S$9=2,$S$10=1,$S$8=1),(ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=2,$S$10=1,$S$8=2),(ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=2,$S$10=2,$S$8=1),(-ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=2,$S$10=2,$S$8=2),(-ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=2,$S$10=3,$S$8=1),(ACOS(1)*180/3.14159)-120+180,IF(AND($S$9=2,$S$10=3,$S$8=2),(ACOS(1)*180/3.14159)+120+180,0))))))","v":0},{"$f":"IF(AND($S$9=2,$S$10=1,$S$8=1),(ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=2,$S$10=1,$S$8=2),(ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=2,$S$10=2,$S$8=1),(-ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=2,$S$10=2,$S$8=2),(-ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=2,$S$10=3,$S$8=1),(ACOS(1)*180/3.14159)+120+180,IF(AND($S$9=2,$S$10=3,$S$8=2),(ACOS(1)*180/3.14159)-120+180,0))))))","v":0}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Pos. VARS",null,{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*SIN(ACOS($B$21))),($H$20)/($N$14*SIN(ACOS(1))))","v":27.800026702272064},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*SIN(ACOS($B$21))),($H$20)/($N$14*SIN(ACOS(1))))","v":27.800026702272064},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*SIN(ACOS($B$21))),($H$20)/($N$14*SIN(ACOS(1))))","v":27.800026702272064}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Neg. VARS",null,{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*SIN(ACOS($B$21))),($H$20)/($N$14*SIN(ACOS(1))))","v":27.800026702272064},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*SIN(ACOS($B$21))),($H$20)/($N$14*SIN(ACOS(1))))","v":27.800026702272064},{"$f":"IF(OR($S$10=1,$S$10=2),($H$20)/($N$14*SIN(ACOS($B$21))),($H$20)/($N$14*SIN(ACOS(1))))","v":27.800026702272064}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(AND($S$10=1,$S$9=4),ACOS($B$21)*180/3.14159,IF(AND($S$10=2,$S$9=4),-ACOS($B$21)*180/3.14159+180,0))","v":0},{"$f":"IF(AND($S$9=4,$S$10=1, $S$8=1),(ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=4,$S$10=1, $S$8=2),(ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=4,$S$10=2, $S$8=1),(-ACOS($B$21)*180/3.14159)-120+180,IF(AND($S$9=4,$S$10=2, $S$8=2),(-ACOS($B$21)*180/3.14159)+120+180,0))))","v":0},{"$f":"IF(AND($S$9=4,$S$10=1,$S$8=1),(ACOS($B$21)*180/3.14159)+120,IF(AND($S$9=4,$S$10=1,$S$8=2),(ACOS($B$21)*180/3.14159)-120,IF(AND($S$9=4,$S$10=2,$S$8=1),(-ACOS($B$21)*180/3.14159)+120+180,IF(AND($S$9=4,$S$10=2,$S$8=2),(-ACOS($B$21)*180/3.14159)-120+180,0))))","v":0}]