## Motor
Graph: Time-Current and Motor Thermal Limit Curves | Table 1: Motor Thermal Limit Curve Points | [7 empty] | Table 2: User Curve Points
| Running (Hot) |  | Running (Cold) |  | Locked (Hot) |  | Locked (Cold) |  | User Curve 1 |  | User Curve 2
| Current (xFLA) | Time (Seconds) | Current (xFLA) | Time (Seconds) | Current (xFLA) | Time (Seconds) | Current (xFLA) | Time (Seconds) | Current (xFLA) | Time (Seconds) | Current (xFLA) | Time (Seconds)
| 1.18 | 6489.68 | 1.36 | 6542.3 | 4.66 | 14.59 | 4.68 | 19.11 | 1 | 3.32
| 1.2 | 5443.79 | 1.37 | 5490.82 | 4.85 | 13.17 | 4.86 | 17.17 | 1.15 | 3.32
| 1.2 | 4587.99 | 1.39 | 4582.89 | 5.03 | 11.9 | 5.05 | 15.41 | 1.51 | 3.32
| 1.21 | 3862.33 | 1.42 | 3829.25 | 5.22 | 10.74 | 5.23 | 13.84 | 1.87 | 3.32
| 1.23 | 3106.38 | 1.44 | 3213.5 | 5.4 | 9.71 | 5.42 | 12.43 | 2.24 | 3.34
| 1.26 | 2544.06 | 1.47 | 2694.56 | 5.58 | 8.78 | 5.6 | 11.16 | 2.6 | 3.32
| 1.28 | 2082.43 | 1.52 | 2261.1 | 5.77 | 7.92 | 5.79 | 10.02 | 2.97 | 3.32
| 1.3 | 1870.13 | 1.57 | 1900.42 | 5.95 | 7.15 | 5.97 | 9 | 3.33 | 3.32
| 1.4 | 1241.91 | 1.62 | 1597.04 | 6.13 | 6.48 | 6.16 | 8.08 | 3.69 | 3.35
| 1.44 | 1059.14 | 1.7 | 1345.03 | 6.38 | 5.69 | 6.34 | 7.26 | 4.06 | 3.37
| 1.51 | 891.68 | 1.76 | 1145.38 | 6.56 | 5.12 | 6.52 | 6.51 | 4.42 | 3.34
| 1.58 | 749.3 | 1.85 | 979.69 | 6.74 | 4.63 | 6.71 | 5.86 | 4.78 | 3.41
| 1.66 | 633.37 | 1.94 | 843.44 | 6.85 | 4.39 | 6.83 | 5.47 | 5.15 | 3.32
| 1.76 | 536.36 | 2.13 | 661.94 |  |  |  |  | 5.51 | 3.18
| 1.88 | 455.68 | 2.29 | 558.11 |  |  |  |  | 5.88 | 2.51
| 2.02 | 387.28 | 2.45 | 478.39 |  |  |  |  | 6.12 | 1.5
| 2.19 | 330.56 | 2.63 | 413.71 |  |  |  |  | 6.18 | 0.97
| 2.36 | 282.43 | 2.77 | 379.93 |  |  |  |  | 6.23 | 0.53
| 2.55 | 243.33 | [6 empty] | 6.24 | 0.3
| 2.73 | 213.07 | [6 empty] | 6.25 | 0.2
| 2.83 | 200.66 | [6 empty] | 6.27 | 0.1
[9 empty] | 6.28 | 0.9
Note on B2: The image below is an example data sheet. Replace with your motor data sheet, if available.
Note on M2: Fill the table with points from the Motor Thermal Capability curves. This will automatically plot the curve in the Coordination Chart in the Chart Worksheet.
Note on V2: You can use this table to plot any additional curves that you would like displayed in the Coordination Chart in the Chart Worksheet
Note on M3: The "running" curves are also known as the "stator" thermal limit curves.
Note on O3: The "Running" curves are also known as the "Stator" thermal limit curves.
Note on Q3: The "Locked" curves are the "Rotor" thermal limit curves.
Note on S3: The "Locked" curves are the "Rotor" thermal limit curves.

## Chart
SEL-710 Setttings |  |  | Relay Thermal Trip Curve Values
SETMETH |  |  | Current I | Trip Time t (seconds)
|  |  | (x FLA) | Cold Stator | Hot Stator | Cold Rotor | Hot Rotor
|  | 3 | 1.01 | #N/A | #N/A
|  |  | 1.1 | #N/A | #N/A
FLS | OFF |  | 1.2 | 4961.8009 | 2614.2661
SF | 1.15 |  | 1.3 | 3021.0058 | 1247.3372
LRA (x FLA) | 6.24 |  | 1.5 | 1754.6615 | 590.844
LRTHOT | 6 |  | 1.7 | 1211.3135 | 370.4478
Acceleration Factor (TD) | 1 |  | 1.9 | 903.3715 | 261.1436
|  |  | 2 | 794.7935 | 225.183
RTC |  | (18) | 2.1 | 705.8957 | 196.7142
|  | 33 | 2.3 | 569.6105 | 154.7381
|  |  | 2.5 | 470.7444 | 125.5247 | 44.8561 | 37.3801
|  |  | 2.7 | 396.3474 | 104.2133 | 38.4569 | 32.0474
I0 Preload (pu of FLA) | 1 |  | 2.9 | 338.7558 | 88.1056 | 33.3354 | 27.7795
|  |  | 3 | 314.6826 | 81.4722 | 31.1501 | 25.9584
* The relay trip curves are considered "Hot" for a I0 preload of 0.9*SF for the stator and 1 for the rotor in the SEL-710 instruction manual |  |  | 3.1 | 293.1506 | 75.5884 | 29.1728 | 24.3107
|  |  | 3.3 | 256.3565 | 65.6414 | 25.7439 | 21.4532
|  |  | 3.5 | 226.2019 | 57.5895 | 22.8858 | 19.0715
Chart Display Options |  |  | 3.7 | 201.1553 | 50.9696 | 20.4785 | 17.0654
MOTOR CURVES | RELAY CURVES |  | 3.9 | 180.1086 | 45.4544 | 18.432 | 15.36
|  |  | 4 | 170.8206 | 43.0343 | 17.5219 | 14.6016
|  |  | 4.1 | 162.2426 | 40.8066 | 16.6776 | 13.898
|  |  | 4.3 | 146.9397 | 36.8502 | 15.1623 | 12.6352
|  |  | 4.5 | 133.727 | 33.4524 | 13.8445 | 11.5371
|  |  | 4.7 | 122.2368 | 30.5113 | 12.6913 | 10.5761
|  |  | 4.9 | 112.1795 | 27.9473 | 11.6764 | 9.7303
|  |  | 5 | 107.6142 | 26.7866 | 11.214 | 9.345
2 |  |  | 5.1 | 103.3244 | 25.6978 | 10.7786 | 8.9821
1 |  |  | 5.3 | 95.4858 | 23.7129 | 9.9804 | 8.317
|  |  | 5.7 | 82.2818 | 20.3824 | 8.6288 | 7.1907
|  |  | 5.9 | 76.6903 | 18.9771 | 8.0537 | 6.7115
|  |  | 6 | 74.1072 | 18.3289 | 7.7875 | 6.4896
|  |  | 6.1 | 71.6532 | 17.7136 | 7.5343 | 6.2786
|  |  | 6.3 | 67.0993 | 16.5734 | 7.0635 | 5.8863
|  |  | 6.5 | 62.9682 | 15.5408 | 6.6355 | 5.5296
|  |  | 6.7 | 59.2091 | 14.6026 | 6.2453 | 5.2044
|  |  | 6.9 | 55.7783 | 13.7475 | 5.8885 | 4.9071
|  |  | 7 | 54.1742 | 13.348 | 5.7214 | 4.7679
|  |  | 7.1 | 52.6386 | 12.9659 | 5.5614 | 4.6345
|  |  | 7.3 | 49.7577 | 12.2495 | 5.2609 | 4.384
|  |  | 7.5 | 47.108 | 11.5913 | 4.984 | 4.1533
|  |  | 7.7 | 44.6651 | 10.9851 | 4.7285 | 3.9404
|  |  | 7.9 | 42.4081 | 10.4255 | 4.4921 | 3.7434
|  |  | 8 | 41.3435 | 10.1617 | 4.3805 | 3.6504
[8 empty] | NUM1 | 7.2
RATING
RATING_1
CURVE:
MINUTES:
AUTO
Running (Hot)
Running (Cold)
Locked (Hot)
Locked (Cold)
Trip (Hot Stator)
Trip (Cold Stator)
Trip (Hot Rotor)
Trip (Cold Rotor)
User Curve 1
User Curve 2
Note on A1: Settings in the grayed-out cells do not affect the trip curves on the Coordination Chart.
Note on Q1: This table displays the values for the relay’s thermal trip curves for SETMETH chosen.
Note on R2: Although the x-axis values in the table start at 1.01 times FLA, the stator thermal trip values are applicable when they exceed the SF setting. The trip time for values of current less than the SF setting is automatically displayed as #N/A.
Note on U3: Trip curves for the rotor starting element start at 2.5 times FLA.
Note on A21: Select the curves you want to display in the Coordination Chart by checking the boxes.

## Calc (hidden)
| ALL THREE METHODS |  | (Source Ref, Second ref for Curve)
Stator Current | Trip (Cold Stator) | Trip (Hot Stator)* |  |  |  | CURVE METHOD (Source Ref) |  | TRUE |  |  | TRUE |  | TRUE |  | TRUE |  | TRUE | TRUE | TRUE | TRUE | TRUE |  | TRUE
(Times FLA) | Tp | Tp |  |  |  | Tp (cold) | Tp (hot) | Thermal Damage Curve Points | [7 empty] | Third ref (used For Trip Plots) (Second Ref on the chart sheet)
1.01 | #NUM! | #NUM! |  |  |  | #NUM! | #NUM! | Running (Hot) |  | Running (Cold) |  | Locked (Hot) |  | Locked (cold) |  | Current I | Trip Time t (seconds) | 0 | 0 | 0 | Curve 1 |  | Curve 2
1.1 | #NUM! | #NUM! |  |  |  | #NUM! | #NUM! | Current (xFLA) | Time (Seconds) | Current (xFLA) | Time (Seconds) | Current (xFLA) | Time (Seconds) | Current (xFLA) | Time (Seconds) | (x FLA) | Cold Stator | Hot Stator | Cold Rotor | Hot Rotor | Current (xFLA) | Time (Seconds) | Current (xFLA) | Time (Seconds)
1.2 | 4961.8009 | 2614.2661 |  |  |  | 2603.1706 | 1371.5546 | 1.18 | 6489.68 | 1.36 | 6542.3 | 4.66 | 14.59 | 4.68 | 19.11 | 1.01 | #N/A | #N/A | 0 | 0 | 1 | 3.32 | 0 | 0
1.3 | 3021.0058 | 1247.3372 |  |  |  | 1584.9474 | 654.4059 | 1.2 | 5443.79 | 1.37 | 5490.82 | 4.85 | 13.17 | 4.86 | 17.17 | 1.1 | #N/A | #N/A | 0 | 0 | 1.15 | 3.32 | 0 | 0
1.5 | 1754.6615 | 590.844 |  |  |  | 920.5697 | 309.9817 | 1.2 | 4587.99 | 1.39 | 4582.89 | 5.03 | 11.9 | 5.05 | 15.41 | 1.2 | 4961.8009 | 2614.2661 | 0 | 0 | 1.51 | 3.32 | 0 | 0
1.7 | 1211.3135 | 370.4478 |  |  |  | 635.5063 | 194.3526 | 1.21 | 3862.33 | 1.42 | 3829.25 | 5.22 | 10.74 | 5.23 | 13.84 | 1.3 | 3021.0058 | 1247.3372 | 0 | 0 | 1.87 | 3.32 | 0 | 0
1.9 | 903.3715 | 261.1436 |  |  |  | 473.9469 | 137.007 | 1.23 | 3106.38 | 1.44 | 3213.5 | 5.4 | 9.71 | 5.42 | 12.43 | 1.5 | 1754.6615 | 590.844 | 0 | 0 | 2.24 | 3.34 | 0 | 0
2 | 794.7935 | 225.183 |  |  |  | 416.9823 | 118.1405 | 1.26 | 2544.06 | 1.47 | 2694.56 | 5.58 | 8.78 | 5.6 | 11.16 | 1.7 | 1211.3135 | 370.4478 | 0 | 0 | 2.6 | 3.32 | 0 | 0
2.1 | 705.8957 | 196.7142 |  |  |  | 370.3428 | 103.2046 | 1.28 | 2082.43 | 1.52 | 2261.1 | 5.77 | 7.92 | 5.79 | 10.02 | 1.9 | 903.3715 | 261.1436 | 0 | 0 | 2.97 | 3.32 | 0 | 0
2.3 | 569.6105 | 154.7381 |  |  |  | 298.8418 | 81.1822 | 1.3 | 1870.13 | 1.57 | 1900.42 | 5.95 | 7.15 | 5.97 | 9 | 2 | 794.7935 | 225.183 | 0 | 0 | 3.33 | 3.32 | 0 | 0
2.5 | 470.7444 | 125.5247 |  |  |  | 246.9724 | 65.8556 | 1.4 | 1241.91 | 1.62 | 1597.04 | 6.13 | 6.48 | 6.16 | 8.08 | 2.1 | 705.8957 | 196.7142 | 0 | 0 | 3.69 | 3.35 | 0 | 0
2.7 | 396.3474 | 104.2133 |  |  |  | 207.9406 | 54.6747 | 1.44 | 1059.14 | 1.7 | 1345.03 | 6.38 | 5.69 | 6.34 | 7.26 | 2.3 | 569.6105 | 154.7381 | 0 | 0 | 4.06 | 3.37 | 0 | 0
2.9 | 338.7558 | 88.1056 |  |  |  | 177.7256 | 46.2239 | 1.51 | 891.68 | 1.76 | 1145.38 | 6.56 | 5.12 | 6.52 | 6.51 | 2.5 | 470.7444 | 125.5247 | 44.8561 | 37.3801 | 4.42 | 3.34 | 0 | 0
3 | 314.6826 | 81.4722 |  |  |  | 165.0958 | 42.7438 | 1.58 | 749.3 | 1.85 | 979.69 | 6.74 | 4.63 | 6.71 | 5.86 | 2.7 | 396.3474 | 104.2133 | 38.4569 | 32.0474 | 4.78 | 3.41 | 0 | 0
3.1 | 293.1506 | 75.5884 |  |  |  | 153.7992 | 39.6569 | 1.66 | 633.37 | 1.94 | 843.44 | 6.85 | 4.39 | 6.83 | 5.47 | 2.9 | 338.7558 | 88.1056 | 33.3354 | 27.7795 | 5.15 | 3.32 | 0 | 0
3.3 | 256.3565 | 65.6414 |  |  |  | 134.4955 | 34.4382 | 1.76 | 536.36 | 2.13 | 661.94 | 0 | 0 | 0 | 0 | 3 | 314.6826 | 81.4722 | 31.1501 | 25.9584 | 5.51 | 3.18 | 0 | 0
3.5 | 226.2019 | 57.5895 |  |  |  | 118.6751 | 30.2139 | 1.88 | 455.68 | 2.29 | 558.11 | 0 | 0 | 0 | 0 | 3.1 | 293.1506 | 75.5884 | 29.1728 | 24.3107 | 5.88 | 2.51 | 0 | 0
3.7 | 201.1553 | 50.9696 |  |  |  | 105.5346 | 26.7408 | 2.02 | 387.28 | 2.45 | 478.39 | 0 | 0 | 0 | 0 | 3.3 | 256.3565 | 65.6414 | 25.7439 | 21.4532 | 6.12 | 1.5 | 0 | 0
3.9 | 180.1086 | 45.4544 |  |  |  | 94.4926 | 23.8473 | 2.19 | 330.56 | 2.63 | 413.71 | 0 | 0 | 0 | 0 | 3.5 | 226.2019 | 57.5895 | 22.8858 | 19.0715 | 6.18 | 0.97 | 0 | 0
4 | 170.8206 | 43.0343 |  |  |  | 89.6197 | 22.5776 | 2.36 | 282.43 | 2.77 | 379.93 | 0 | 0 | 0 | 0 | 3.7 | 201.1553 | 50.9696 | 20.4785 | 17.0654 | 6.23 | 0.53 | 0 | 0
4.1 | 162.2426 | 40.8066 |  |  |  | 85.1193 | 21.4089 | 2.55 | 243.33 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 180.1086 | 45.4544 | 18.432 | 15.36 | 6.24 | 0.3 | 0 | 0
4.3 | 146.9397 | 36.8502 |  |  |  | 77.0908 | 19.3332 | 2.73 | 213.07 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 170.8206 | 43.0343 | 17.5219 | 14.6016 | 6.25 | 0.2 | 0 | 0
4.5 | 133.727 | 33.4524 |  |  |  | 70.1589 | 17.5506 | 2.83 | 200.66 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 162.2426 | 40.8066 | 16.6776 | 13.898 | 6.27 | 0.1 | 0 | 0
4.7 | 122.2368 | 30.5113 |  |  |  | 64.1306 | 16.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 146.9397 | 36.8502 | 15.1623 | 12.6352 | 6.28 | 0.9 | 0 | 0
4.9 | 112.1795 | 27.9473 |  |  |  | 58.8541 | 14.6623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 133.727 | 33.4524 | 13.8445 | 11.5371 | 0 | 0 | 0 | 0
5 | 107.6142 | 26.7866 |  |  |  | 56.4589 | 14.0534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 | 122.2368 | 30.5113 | 12.6913 | 10.5761 | 0 | 0 | 0 | 0
5.1 | 103.3244 | 25.6978 |  |  |  | 54.2083 | 13.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 112.1795 | 27.9473 | 11.6764 | 9.7303 | 0 | 0 | 0 | 0
5.3 | 95.4858 | 23.7129 |  |  |  | 50.0959 | 12.4408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 107.6142 | 26.7866 | 11.214 | 9.345 | 0 | 0 | 0 | 0
5.7 | 82.2818 | 20.3824 |  |  |  | 43.1685 | 10.6935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 103.3244 | 25.6978 | 10.7786 | 8.9821 | 0 | 0 | 0 | 0
5.9 | 76.6903 | 18.9771 |  |  |  | 40.235 | 9.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 95.4858 | 23.7129 | 9.9804 | 8.317 | 0 | 0 | 0 | 0
6 | 74.1072 | 18.3289 |  |  |  | 38.8798 | 9.6161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7 | 82.2818 | 20.3824 | 8.6288 | 7.1907 | 0 | 0 | 0 | 0
6.1 | 71.6532 | 17.7136 |  |  |  | 37.5923 | 9.2933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 76.6903 | 18.9771 | 8.0537 | 6.7115 | 0 | 0 | 0 | 0
6.3 | 67.0993 | 16.5734 |  |  |  | 35.2031 | 8.6951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 74.1072 | 18.3289 | 7.7875 | 6.4896 | 0 | 0 | 0 | 0
6.5 | 62.9682 | 15.5408 |  |  |  | 33.0358 | 8.1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1 | 71.6532 | 17.7136 | 7.5343 | 6.2786 | 0 | 0 | 0 | 0
6.7 | 59.2091 | 14.6026 |  |  |  | 31.0636 | 7.6611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 67.0993 | 16.5734 | 7.0635 | 5.8863 | 0 | 0 | 0 | 0
6.9 | 55.7783 | 13.7475 |  |  |  | 29.2637 | 7.2125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5 | 62.9682 | 15.5408 | 6.6355 | 5.5296 | 0 | 0 | 0 | 0
7 | 54.1742 | 13.348 |  |  |  | 28.4221 | 7.0029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 59.2091 | 14.6026 | 6.2453 | 5.2044 | 0 | 0 | 0 | 0
7.1 | 52.6386 | 12.9659 |  |  |  | 27.6164 | 6.8024 | [8 empty] | 6.9 | 55.7783 | 13.7475 | 5.8885 | 4.9071
7.3 | 49.7577 | 12.2495 |  |  |  | 26.105 | 6.4266 | [8 empty] | 7 | 54.1742 | 13.348 | 5.7214 | 4.7679
7.5 | 47.108 | 11.5913 |  |  |  | 24.7148 | 6.0813 | [8 empty] | 7.1 | 52.6386 | 12.9659 | 5.5614 | 4.6345
7.7 | 44.6651 | 10.9851 |  |  |  | 23.4332 | 5.7633 | [8 empty] | 7.3 | 49.7577 | 12.2495 | 5.2609 | 4.384
7.9 | 42.4081 | 10.4255 |  |  |  | 22.2491 | 5.4697 | [8 empty] | 7.5 | 47.108 | 11.5913 | 4.984 | 4.1533
8 | 41.3435 | 10.1617 |  |  |  | 21.6905 | 5.3313 | RTC Calculator for AUTO and CURVE | [7 empty] | 7.7 | 44.6651 | 10.9851 | 4.7285 | 3.9404
[16 empty] | 7.9 | 42.4081 | 10.4255 | 4.4921 | 3.7434
|  |  | RATING exception (I0 > FLA) | [5 empty] | AUTO | 18.0236 | (divided the formula by 60 REMEMBER TO MARK in APP GUIDE) |  |  |  |  | 8 | 41.3435 | 10.1617 | 4.3805 | 3.6504
| Trip (Cold Rotor) | Trip (Hot Rotor)* | Trip (Hot Rotor I0 >FLA) |  |  | Rotor (cold) | Rotor (hot) |  | CURVE | 17.3132 | (divided the formula by 60 REMEMBER TO MARK in APP GUIDE) |  |  |  |  | #REF! | #REF! | #REF! | #REF! | #REF!
| Tp | Tp |  | Test column (ignore) | I | Tp | Tp | [8 empty] | #REF! | #REF! | #REF! | #REF! | #REF!
2.5 | 44.8561 | 37.3801 | 37.3801 | 37.3801 | 2.5 | 43.2 | 36 | [8 empty] | #REF! | #REF! | #REF! | #REF! | #REF!
2.7 | 38.4569 | 32.0474 | 32.0474 | 32.0474 | 2.7 | 37.037 | 30.8642 | Chosen RTC |  | 18.0236 | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF!
2.9 | 33.3354 | 27.7795 | 27.7795 | 27.7795 | 2.9 | 32.1046 | 26.7539 |  |  | 18.0236 | [5 empty] | 0 | 0 | 0 | 0 | 0
3 | 31.1501 | 25.9584 | 25.9584 | 25.9584 | 3 | 30 | 25 | Text format |  | 18 | [5 empty] | 0 | 0 | 0 | 0 | 0
3.1 | 29.1728 | 24.3107 | 24.3107 | 24.3107 | 3.1 | 28.0957 | 23.4131 | [8 empty] | 0 | 0 | 0 | 0 | 0
3.3 | 25.7439 | 21.4532 | 21.4532 | 21.4532 | 3.3 | 24.7934 | 20.6612
3.5 | 22.8858 | 19.0715 | 19.0715 | 19.0715 | 3.5 | 22.0408 | 18.3673
3.7 | 20.4785 | 17.0654 | 17.0654 | 17.0654 | 3.7 | 19.7224 | 16.4354
3.9 | 18.432 | 15.36 | 15.36 | 15.36 | 3.9 | 17.7515 | 14.7929
4 | 17.5219 | 14.6016 | 14.6016 | 14.6016 | 4 | 16.875 | 14.0625
4.1 | 16.6776 | 13.898 | 13.898 | 13.898 | 4.1 | 16.0619 | 13.3849
4.3 | 15.1623 | 12.6352 | 12.6352 | 12.6352 | 4.3 | 14.6025 | 12.1687
4.5 | 13.8445 | 11.5371 | 11.5371 | 11.5371 | 4.5 | 13.3333 | 11.1111
4.7 | 12.6913 | 10.5761 | 10.5761 | 10.5761 | 4.7 | 12.2227 | 10.1856
4.9 | 11.6764 | 9.7303 | 9.7303 | 9.7303 | 4.9 | 11.2453 | 9.3711
5 | 11.214 | 9.345 | 9.345 | 9.345 | 5 | 10.8 | 9
5.1 | 10.7786 | 8.9821 | 8.9821 | 8.9821 | 5.1 | 10.3806 | 8.6505
5.3 | 9.9804 | 8.317 | 8.317 | 8.317 | 5.3 | 9.612 | 8.01
5.7 | 8.6288 | 7.1907 | 7.1907 | 7.1907 | 5.7 | 8.3102 | 6.9252
5.9 | 8.0537 | 6.7115 | 6.7115 | 6.7115 | 5.9 | 7.7564 | 6.4637
6 | 7.7875 | 6.4896 | 6.4896 | 6.4896 | 6 | 7.5 | 6.25
6.1 | 7.5343 | 6.2786 | 6.2786 | 6.2786 | 6.1 | 7.2561 | 6.0468
6.3 | 7.0635 | 5.8863 | 5.8863 | 5.8863 | 6.3 | 6.8027 | 5.6689
6.5 | 6.6355 | 5.5296 | 5.5296 | 5.5296 | 6.5 | 6.3905 | 5.3254
6.7 | 6.2453 | 5.2044 | 5.2044 | 5.2044 | 6.7 | 6.0147 | 5.0123
6.9 | 5.8885 | 4.9071 | 4.9071 | 4.9071 | 6.9 | 5.6711 | 4.7259
7 | 5.7214 | 4.7679 | 4.7679 | 4.7679 | 7 | 5.5102 | 4.5918
7.1 | 5.5614 | 4.6345 | 4.6345 | 4.6345 | 7.1 | 5.3561 | 4.4634
7.3 | 5.2609 | 4.384 | 4.384 | 4.384 | 7.3 | 5.0666 | 4.2222
7.5 | 4.984 | 4.1533 | 4.1533 | 4.1533 | 7.5 | 4.8 | 4
7.7 | 4.7285 | 3.9404 | 3.9404 | 3.9404 | 7.7 | 4.5539 | 3.7949
7.9 | 4.4921 | 3.7434 | 3.7434 | 3.7434 | 7.9 | 4.3262 | 3.6052
8 | 4.3805 | 3.6504 | 3.6504 | 3.6504 | 8 | 4.2188 | 3.5156
Note on F50: Logic is: IF Curve, Then Column L, Else IF Rating, then IF ( I0<1) Then I^2t, Else Column G Else Rating_1 formula