## Calculations
Fault Locator
By: Alexandro Rangel Werdene
Schweitzer Engineering Labs.
This program calculates the fault location using V2 and I2 from each
end of the line.
Instructions:
1.- Insert I2 and V2 from the left relay at I2L and V2L respectively
2.- Insert I2 and V2 from the right relay at I2R and V2R respectively
3.- Insert the line impedance in Z2L (obtain from relay settings)
4.- Insert the total line distance in miles
5.- The answer is expressed in per unit (m) and in miles
Disclaimer: This program is provided as is, without
warranty, either expressed or implied. It does not
purport to be free of bugs. Therefore, its use is the
sole responsibility of the user.
| Magnitude | Angle | Real | Imaginary | Rectangular
I2L | 369.099 | 164.7 | -356.0172 | 97.3953 | -356.017178595355+97.3952788691693i | -
V2L | 8299.999 | 64 | 3638.4801 | 7459.9897 | 3638.4800799782+7459.98968548904i | -
I2R | 805 | 160.1998 | -757.4081 | 272.6867 | -757.408067156724+272.686669652031i | -
V2R | 15799.9653 | 63.3999 | 7074.6027 | 14127.5936 | 7074.6027079253+14127.5935674205i | -
Z2L | 67.3318 | 75.577 | 16.7709 | 65.2097 | 16.7709159547463+65.2097206655483i | -
Z2S_L |  |  |  |  | 4.17512028489288+22.0961997423434i | -
Z2S_R |  |  |  |  | 2.32391454467663+19.4892221581129i | -
Line Distance | 82 | miles
A | 2320240659.2001 |  | Fault | 63.9516 | miles from left
B | -7985054492.5038 |  |  | 18.0484 | miles from right
C | 4816261686.4631 |  | m (distance in pu) | 0.7799 | per unit from left
m1 | 2.6616 |  | 1-m | 0.2201 | per unit from right
m2 | 0.7799