## Instructions
Line Impedance Calculator | Disclaimer: This program is provided as is, without warranty, either expressed or implied. It does not purport to be free of errors. Therefore, its use is the sole responsibility of the user.
Schweitzer Engineering Laboratories, Inc.
Line Impedance Calculator
This program calculates the positive-, negative-, and zero-sequence line impedances using aligned voltage and current data from relays at each end of the line, as well as a known fault location, during a phase-to-ground fault. The calculator can be found on the next tab.
Instructions:
1. Select the symmetrical component network to be used (negative- or zero-sequence).
2. Insert Ix and Vx from Relay S at IxS and VxS, respectively (x = 0 or 2).
3. Insert Ix and Vx from Relay R at IxR and VxR, respectively (x = 0 or 2).
4. Insert the line length in miles, fault location in per unit, CT ratio, and PT ratio.
5. Insert the error tolerance for magnitude (%) and angle (degrees).
6. Insert the line impedance settings in polar or rectangular form.
7. Specify the line impedance format in the corresponding green rectangles.
8. The comparison box compares the relay settings with the calculated values and computes the error.

## Calculator
Line Impedance Calculator
| Magnitude | Angle | Real |  | Imaginary | Rectangular
I2S | 4228 | -86 | 294.9304 |  | -4217.7008 | 294.930370990161-4217.70080449854i | - | 1
V2S | 29950 | -180 | -29950 |  | 0 | -29950 | -
I2R | 3396 | -86 | 236.893 |  | -3387.7275 | 236.892984835049-3387.72751468236i | - |  | 1
V2R | 25230 | -179 | -25226.1573 |  | -440.3242 | -25226.1573487958-440.324214412661i | -
Z2L | 13.6961 | 80.6747 | 2.2193 |  | 13.5151 | 2.21931354684493+13.5150696981057i | -
Line Length | 2.29 | miles |  | Fault Location
Fault Location in pu (m) | 0.4 | per unit |  | 0.916 | miles from S |  |  | 1
CTR | 0 | unitless |  | 1.374 | miles from R
PTR | 0 | unitless | [6 empty] | 1
Error Tolerance - Magnitude | 6 | %
Error Tolerance - Angle | 6 | Degrees
LINE IMPEDANCE SETTINGS
Polar Coordinates |  | OR | Rectangular Coordinates |  |  |  |  | 1
Z2MAG | 12 |  | R2 |  | 1.1545
Z2ANG | 75 |  | X2 |  | 13.6046
RESULTS COMPARISON BOX
| Relay Settings | Calculated | Error
Magnitude | 12 | 13.6961 | 14.134 |  | %
Angle | 75 | 80.6747 | 5.6747 |  | Degrees
3.10582854123025+11.5911099154688i
2.21931354684493+13.5150696981057i
| Mag | Ang
Relay settings | 13.6535 | 85.1493 |  | 1.1545 | 13.6046
Calculated settings | 13.6961 | 80.6747 |  | 2.2193 | 13.5151

## Leave Alone (hidden)
1
1
1